STANDARD SPECIFICATIONS

OUTPUT RATINGS

The following 3 phase ratings are available:

50Hz
415/240V
400/230V
380/220V
240/120


230/115V
220/110V



60Hz
440/254V
416/240V
400/230V
380/220V


240/120V
230/115V
230/110V














ENGINE
Yanmar TNE range generator specification diesel engine (technical details are supplied on the reverse of this sheet). Lubricating oil drain valve fitted as standard on acoustic canopy variants. EPA approved versions are available.

Governor
Compliant with BS5514, Class A1. 

Electrical System
12 Volt DC. Energised to run shutdown solenoid.  Oil pressure and water temperature shutdown via. Senders to control  module.

ALTERNATOR
Newage alternators have been carefully selected to match the overload performance of the engine and incorporate the following; screen protected and drip-proof, self regulating brushless alternator with fully interconnected damper windings. IC06 cooling system and sealed-for-life bearings. Twelve wire re-connectable windings provide a wide range of 3 phase voltages.

Insulation System
The insulation system is Class H.  All windings are impregnated in either a triple dip thermo-setting moisture, oil and acid resisting polyester varnish or vacuum pressure impregnated with a special polyester resin.  Heavy coat of anti-tracking varnish for additional protection against moisture or condensation.

Electrical Characteristics
Electrical design in accordance with BS5000 Part 99, IEC34-1, VDEO530, UTE5100, NEMA MG-122, CEMA, CSA 22.2 and AS1359

Automatic Voltage Regulator
The fully sealed automatic voltage regulator maintains the voltage within the limits of +/-1.50/0 from no load to full load including cold to hot variations at any power factor between 0.8 lagging and unity and inclusive of a speed variation of 4.00/0.  Nominal adjustment is by means of a trimmer incorporated in the AVR.

Radio Interference

Suppression is in line with the provisions of BS EN 50081 and VDE Class G.

[image: image1.jpg]ROADCROYYN




[image: image2.jpg]



[image: image3.jpg]



CONTROL SYSTEM

Set mounted, manually operated control panel of fabricated sheet steel construction with a hinged lockable door.  The control panel is isolated  from the engine and comprises of the following instrumentation and controls:  

Low oil pressure lamp, high water temperature lamp, battery charge ammeter, voltmeter and selector switch, ammeter and selector switch, dual frequency/rpm meter and hours counter. A key start control module and emergency stop button are fitted as standard.

Shutdown Protection Devices with Indicators for:
High coolant temperature low oil pressure.

Circuit Breaker
Three pole moulded case circuit breaker or a 3 pole miniature circuit breaker mounted on the baseframe in a sheet steel box with adequate access for incoming and outgoing cables.

Output Sockets

A wide range of options are available.
FUEL SYSTEM

The baseframe design incorporates a plastic fuel tank with a capacity of 12 hours at a 75% load.  The tank is supplied complete with level indicator and  fuel fill cap, bosses for vent,  fuel feed and return lines to engine. Optional remote fuel tank connections available.

COOLING RADIATOR

Radiator and cooling fan complete with protection guards, designed to cool the engine at specified output, in air-on temperatures up to 52°C (126°F).Coolant drain valve fitted as standard  on acoustic canopy variants.

ENGINE FILTRATION SYSTEM
Sealed paper mesh type dry air filters.  Cartridge type fuel filters including water seperator.  Full flow lube oil filters.  All filters have replacement elements.

EXHAUST SYSTEM

Heavy-duty industrial capacity exhaust silencer.

ELECTRICAL SYSTEM

12 Volt system with battery charging alternator, axial type starter motor, high capacity maintenance free lead acid starting batteries, battery rack mounted on the generator set baseframe, and heavy duty interconnecting cables with terminations.

MOUNTING ARRANGEMENT

Baseframe

The complete generator set is mounted, as a whole, on a baseframe.  The baseframe incorporates specially designed fork lift pocket and an optional centre point lift.

(Standard on acoustic canopy variants).

[image: image4.jpg]



Coupling

The engine and alternator are directly coupled by means of an SAE flange so that there is no possibility of misalignment after prolonged use.  The engine flywheel is flexibly coupled to the alternator rotor and a full torsional analysis has been carried out to guarantee no harmful vibration will occur in the assembly.

Anti-Vibration Mounts

Anti-Vibration mounts are affixed between engine/alternator feet and the baseframe, thus ensuring complete vibration isolation of the rotating assemblies.

Safety Guards

The fan, fan drive and battery charging alternator drive are fully guarded for personnel protection. 

GENERAL ARRANGEMENT

The generator set is designed and constructed for installation in a weather-protected building. Sound attenuated enclosures achieving 75dB(A) at 1m or better are available. 

DOCUMENTATION

A full set of operation and maintenance manuals and circuit wiring diagrams are supplied with each generator set.

FACTORY TESTS

The generator set is load tested before despatch.  All protective devices and control functions of the generator/system are simulated and checked before despatch.  A test certificate is provided with each generator set.

EQUIPMENT FINISH

Primer on all equipment.  Final coat to manufacturer’s standard.

QUALITY STANDARDS

The equipment meets the following standards:

BS4999, BS5000, BS5514, IEC 34, VDE0530, NEMA MG-122

PRODUCT ENDORSEMENT

All equipment is guaranteed* for a period of 12 months from date of commissioning, or 18 months from date of ex works shipment, whichever occurs first.  Where equipment is supplied by an authorised Broadcrown Distributor or Dealer, the 12 month guarantee* period will commence from the date of delivery to the first retail purchaser or 18 months from  date of ex works shipment, whichever occurs first.

Please see Broadcrown Warranty statement for a full specification of terms.  Extended warranty terms are available, for details please contact Broadcrown Customer Services Department.

*Equipment must only be used in accordance with recommended operating practices and subject to any specified load limitations.

MISCELLANEOUS

Shrink wrapped for export.

Rating Definitions:


Prime Power (models with suffix ‘P’). All ratings are suitable for continuous power (at variable load in lieu of main power network). There is no limitation to the annual hours of operation.





SPECIFICATION NOTES








Ratings at 0.8 p.f 25(C(77(F) 3 phase, 1.0 p.f single phase. Ambient, 177m (600ft) above sea level.


All ratings are in compliance with BC5514, ISO 3046, DIN6271, ISO 8528





Broadcrown Limited


Airfield Industrial Estate, Hixon Stafford, Staffordshire, ST18 0PF, England


Telephone: +44 (0) 1889 272200, Fax: + 44 (0) 1889 272220, E-mail: info@broadcrown.co.uk


Website: www,broadcrown.co.uk





In line with the Broadcrown Limited policy of continual development and improvement the information given here is only intended for the assistance of clients and is not binding upon the company which reserves the rights to alter specification of its products without notice.











[image: image1.jpg]

